EDS150

Insulation fault locator EDS150 for insulation fault location systems featuring six measuring channels for use in unearthed AC, DC and AC/DC systems (IT systems).

Standards:
This version complies with the requirements of: DIN EN 61557-9 (VDE 0413 Part 9)

The locating current signals generated by a locating current injector are detected by integrated measuring current transformers and evaluated by the EDS151 insulation fault locator. When the locating current exceeds the response value, it is indicated by the LEDs. The measured values are made available via the BMS bus interface.

Supply voltage: AC 17…24 V, DC 14…28 V
Nominal system voltage: AC 20…265 V / DC 20…308 V or refer to PGH... locating current injector resp. IRDH575
 
Channels: 6 per device, up to 528 per system
Measuring current transformers: integrated 
Response values: 5 mA for all channels
Response time: in the AC system acc. to IEC 61557-9 ≤ 8 s
Display elements:	1 alarm LED for each channel; ON/COM LED: Power On LED and bus activity 
Interface: RS-485/BMS bus protocol
Width of enclosure: 12 TE

Remote parameter setting, indication and visualisation possible via interface and gateway.

Manufacturer:
Bender GmbH & Co. KG
Londorfer Straße 65
35305 Grünberg

Type: EDS150
Article number: B91080103
Unit: piece